## Slide 1
University AI infrastructure
Compute Commons / University AI infrastructure / illustrative model
A lease pilot preserves the option to build
25 MW baseline facility
6.25 MW conditional first phase
No signed demand or firm grid terms
Notes: 0:00–0:50. Recommend a lease pilot and defer an irreversible 25 MW construction commitment. No member has signed a long-term commitment, and grid costs/date are unknown under the assignment. The site and model compare the US, China and Singapore. Massachusetts is a scenario assumption for a hypothetical US consortium, not a proven globally best location.

## Slide 2
Base-case cost per productive GPU-hour
Compute Commons / University AI infrastructure / illustrative model
Chart: 
| Build & own | Lease capacity | Phased hybrid
USD / productive GPU-hour | 3.69 | 3.37 | 3.46
$3.37
Lease case
$59.8m before opening
$239.1m annual opex
Assumed prices and demand. Unit cost includes lifecycle capital costs.
Notes: 0:50–1:50. All inputs are illustrative constant USD, not vendor quotes. 10-year window, 8% real discount rate, no tax/residual, IT refresh in operating years 5 and 9. Demand is equal across strategies: roughly 71 million productive GPU-hours annually. Full-scale upfront facility/grid/IT is $830m. Rental is $3 per allocated GPU-hour before availability and efficiency adjustment. Sources: data/model-results.json and lib/model.ts in project.

## Slide 3
Low utilization raises ownership cost
Compute Commons / University AI infrastructure / illustrative model
Chart: 
| Build & own | Lease capacity | Phased hybrid
Base case | 3.69 | 3.37 | 3.46
Half utilization | 7.27 | 3.37 | 4.36
USD per productive GPU-hour. Fixed demand commitments could change the lease result.
Notes: 1:50–2:50. Halving utilization raises owned cost from $3.69 to $7.27, while leased unit cost remains $3.37 under a flexible usage assumption. The half-use case halves productive output, but fixed staffing and maintenance remain and electricity declines less than half. A one-year grid delay increases build cost to $4.00 because bridge leases preserve the same demand. A real lease may have minimum commitments. Sources: deterministic model output.

## Slide 4
First-phase resilience remains unverified
Compute Commons / University AI infrastructure / illustrative model
6.25 MW
Conditional total site demand
300 MWh
Energy for 48 hours at full load
One failed transformer: transfer to the independent path
One failed generator: four remaining units must carry load
Cooling and fuel logistics remain critical dependencies
Notes: 2:50–3:50. The conditional first phase has 5 MW IT and 6.25 MW total power. Proposed two 8 MVA transformer paths should each carry total load at assumed PF .95. Five 2 MW generators provide 8 MW with one failed before derating. 48 hours needs 300 MWh and assumed fuel of 90,000 litres including reserve. Verify transfer, protection, generator derating, cooling, fuel permits and logistics. No renewable contribution is credited as firm backup. All quantities are concept calculations, not certified engineering.

## Slide 5
Evidence needed before construction
Compute Commons / University AI infrastructure / illustrative model
Signed demand
GPU-hour commitments and measured job traces
Binding power terms
Tariff, upgrade liability, energization date and outage tests
Comparable supplier bids
Hardware benchmarks, cloud scope, replacement and exit costs
Notes: 3:50–5:00. Three findings could reverse the recommendation. First signed, benchmarked demand with large-cluster concurrency data. Second firm utility terms and verified resilience. Third comparable cloud and hardware offers with complete support and exit costs. Development equity bears early-stage risk. Construction debt follows signed commitments and grid terms. A member nonprofit owns the shell and electrical/cooling assets and contracts construction/operations. Published quotas, metering, smaller-institution teaching reservations and appeals guard against cross-subsidy. Ask the committee to approve a bounded evidence and lease-pilot stage, not the 25 MW capital commitment.